
Fault Condition One Report

Fault condition one of ASHRAE Guideline 36 is related to flagging poor performance of a AHU variable supply fan attempting to control to a duct pressure setpoint. Fault condition equation as defined by ASHRAE:




## Dataset Plot



## Dataset Statistics

* Total time calculated in dataset: 30 days 23:45:00
* Total time in hours calculated in dataset: 743.75
* Total time in hours for when fault flag is True: 2.0
* Percent of time in the dataset when the fault flag is True: 32.53%
* Percent of time in the dataset when the fault flag is False: 67.47%

## Time-of-day Histogram Plots



* Average duct system pressure for when in fault condition (fan VFD speed > 95%): 0.64"WC

## VFD Speed Statistics

* count 2976.000000  
  mean 63.073253  
  std 12.335316  
  min 28.000000  
  25% 54.000000  
  50% 63.000000  
  75% 71.000000  
  max 96.000000  
  Name: supply\_vfd\_speed, dtype: float64

## Duct Pressure Statistics

* count 2976.000000  
  mean 1.093586  
  std 0.395355  
  min 0.050710  
  25% 0.850710  
  50% 1.150710  
  75% 1.350710  
  max 1.950710  
  Name: duct\_static, dtype: float64

## Duct Pressure Setpoints Statistics

* count 2976.0  
  mean 1.0  
  std 0.0  
  min 1.0  
  25% 1.0  
  50% 1.0  
  75% 1.0  
  max 1.0  
  Name: duct\_static\_setpoint, dtype: float64

## Suggestions based on data analysis

* Fan is appears to generate good duct static pressure (GOOD)
* No duct pressure setpoint reset detected (BAD)

Report generated: Thu Dec 22 08:12:05 2022